## Slide 1
Process Control: Designing Process and Control Systems for Dynamic Performance
Chapter 7. The Feedback Loop
Copyright © Thomas Marlin 2013
The copyright holder provides a royalty-free license for use of this material at non-profit educational institutions

## Slide 2
CHAPTER 7: THE FEEDBACK LOOP
When I complete this chapter, I want to be
able to do the following.
Identify the major elements in the feedback loop
Select appropriate candidate variables to be controlled and manipulated
Evaluate the control performance data using standard measures of dynamic performance

## Slide 3
Outline of the lesson.
Typical loop elements
Relating variables to control objectives
- Examples
Typical control performance measures
Five approaches to feedback control
CHAPTER 7: THE FEEDBACK LOOP

## Slide 4
CHAPTER 7: THE FEEDBACK LOOP
TC
A
v1
v2
The Concept: We show limited detail in the piping and instrumentation (P&I) drawing. We see the sensor location, variable measured, connection to the final element (valve) and the location of the final element.

## Slide 5
CHAPTER 7: THE FEEDBACK LOOP
T
A
v1
v2
The Reality: Many elements in the loop affect the safety, reliability, accuracy, dynamics and cost. Engineers need to understand the details!
4-20 mA
4-20 mA
3-15 psi

## Slide 6
CHAPTER 7: THE FEEDBACK LOOP
Sensor &
transmitter
electronic
transmission
input and A/D
conversion
computing
network
electronic
transmission
I/P
conversion
pneumatic
transmission
final
element
THE PROCESS
Make a step
(without feedback control)
What affects the response to the computer?
output
and D/A

## Slide 7
CHAPTER 7: THE FEEDBACK LOOP
Class exercise: Given the following dynamics, sketch the responses for a step in manual station to the displayed value.

## Slide 8
CHAPTER 7: THE FEEDBACK LOOP
Class exercise: Given the following dynamics, sketch the responses for a step in manual station to the displayed value.
What you see (from the display) is not always what is occurring!!

## Slide 9
CHAPTER 7: THE FEEDBACK LOOP
The engineer must decide what measurement to control and what valve to adjust (and provide the equipment to support the decisions).

## Slide 10
CHAPTER 7: THE FEEDBACK LOOP
The engineer must decide what measurement to control and what valve to adjust (and provide the equipment to support the decisions).
CV to control ? Use seven categories of control objectives!

## Slide 11
CHAPTER 7: THE FEEDBACK LOOP
The engineer must decide what measurement to control and what valve to adjust (and provide the equipment to support the decisions).
MV to adjust ?
1. Causal relationship
2. Automated
3. Fast dynamics
4. Compensate for large disturbances
5. Can adjust quickly with little adverse affect on process performance

## Slide 12
CHAPTER 7: THE FEEDBACK LOOP
The engineer must decide what measurement to control and what valve to adjust (and provide the equipment to support the decisions).
We could use either valve.
We will revisit this choice
later (Chapter13)

## Slide 13
CHAPTER 7: THE FEEDBACK LOOP
The figure shows the feedback loop We’ll see the calculation in the next chapter.
Explain, including the
feedback concept.

## Slide 14
FT
1
FT
2
PT
1
AT
1
TI
1
TI
2
TI
3
TI
4
PI
2
PI
3
PI
4
TI
5
TI
6
TI
7
TI
8
TI
9
FI
3
TI
10
TI
11
PI
5
PI
6
Class exercise on the feedback loop: Using the methods just described, select ONE variable to be controlled and for that variable, ONE valve to be manipulated.
feed
air
fuel
Flue gas
burner

## Slide 15
FT
1
FT
2
PT
1
AT
1
TI
1
TI
2
TI
3
TI
4
PI
2
PI
3
PI
4
TI
5
TI
6
TI
7
TI
8
TI
9
FI
3
TI
10
TI
11
PI
5
PI
6
Class exercise on the feedback loop: Using the methods just described, select ONE variable to be controlled and for that variable, ONE valve to be manipulated.
feed
air
fuel
Flue gas
burner
TC

## Slide 16
FT
1
FT
2
PT
1
AT
1
TI
1
TI
2
TI
3
TI
4
PI
2
PI
3
PI
4
TI
5
TI
6
TI
7
TI
8
TI
9
FI
3
TI
10
TI
11
PI
5
PI
6
Class exercise on the feedback loop: Using the methods just described, select ONE variable to be controlled and for that variable, ONE valve to be manipulated.
feed
air
fuel
Flue gas
burner
AC
O2

## Slide 17
CHAPTER 7: THE FEEDBACK LOOP
Music: “I cannot define good music, but I know what I like.”
Control Performance: We must be able to define what we desire, so that we can design equipment and controls to achieve our objectives.
0
5
10
15
20
25
30
35
40
45
50
0
0.5
1
1.5
Time
Controlled Variable
0
5
10
15
20
25
30
35
40
45
50
0
0.5
1
1.5
2
Time
Manipulated Variable
Controlled variable, value from a sensor
Manipulated variable, usually a valve
Set point
entered by
person

## Slide 18
0
5
10
15
20
25
30
35
40
45
50
0
0.5
1
1.5
2
Time
Manipulated Variable
0
5
10
15
20
25
30
35
40
45
50
0
0.5
1
1.5
Time
Controlled Variable
CHAPTER 7: THE FEEDBACK LOOP
Let’s be sure we understand the
variables in the plot. We will see this
plot over and over and over …!

## Slide 19
CHAPTER 7: THE FEEDBACK LOOP
Set point Change
0
5
10
15
20
25
30
35
40
45
50
0
0.5
1
1.5
Time
0
5
10
15
20
25
30
35
40
45
50
0
0.5
1
1.5
2
Time
= IAE =


|SP(t)-CV(t)| dt
Return to set point, “zero offset
Rise time
D
B
B/A = Decay ratio
C/D = Maximum overshoot of manipulated variable
C
A
0


## Slide 20
CHAPTER 7: THE FEEDBACK LOOP
Disturbance Response
0
5
10
15
20
25
30
35
40
45
50
-0.2
0
0.2
0.4
0.6
0.8
Time
0
5
10
15
20
25
30
35
40
45
50
-1.5
-1
-0.5
0
Time
= IAE =
|SP(t)-CV(t)| dt
Maximum CV deviation from set point


0


## Slide 21
CHAPTER 7: THE FEEDBACK LOOP
Disturbance Response
0
100
200
300
400
500
600
700
800
900
1000
-20
-10
0
10
20
S-LOOP plots deviation variables (IAE = 5499.9786)
Time
Controlled Variable
0
100
200
300
400
500
600
700
800
900
1000
-20
-10
0
10
20
Time
Manipulated Variable
Variance or standard deviation of CV
Variance or standard deviation of MV
Often, the process is subject to many large and small disturbances and sensor noise. The performance measure characterizes the variability.

## Slide 22
CHAPTER 7: THE FEEDBACK LOOP
To reduce the variability in the CV,
we increase the variability in the MV.
We must design plant with MV’s
that can be adjusted at low cost.
0
100
200
300
400
500
600
700
800
900
1000
-20
-10
0
10
20
Time
Controlled Variable
0
100
200
300
400
500
600
700
800
900
1000
-20
-10
0
10
20
Time
Manipulated Variable

## Slide 23
CHAPTER 7: THE FEEDBACK LOOP
Class exercise: For each of the performance measures below, determine a good value, i.e., large/small, positive/negative, etc.
Offset
IAE
Decay ratio
Rise time
Settling time
MV overshoot
Maximum CV deviation
CV variance
MV variance
Can we achieve good values for all at the same time?
What are the tradeoffs?

## Slide 24
Class exercise: Comment on the quality of control for the four responses below.
0
20
40
60
80
100
120
-0.5
0
0.5
1
1.5
S-LOOP plots deviation variables (IAE = 17.5417)
Time
Controlled Variable
0
20
40
60
80
100
120
-0.5
0
0.5
1
1.5
2
Time
Manipulated Variable
A
0
20
40
60
80
100
120
-1
0
1
2
3
S-LOOP plots deviation variables (IAE = 43.9891)
Time
Controlled Variable
0
20
40
60
80
100
120
-1
0
1
2
3
4
Time
Manipulated Variable
B
0
20
40
60
80
100
120
-0.5
0
0.5
1
1.5
S-LOOP plots deviation variables (IAE = 34.2753)
Time
Controlled Variable
0
20
40
60
80
100
120
-0.5
0
0.5
1
Time
Manipulated Variable
C
0
20
40
60
80
100
120
-0.5
0
0.5
1
1.5
S-LOOP plots deviation variables (IAE = 24.0376)
Time
Controlled Variable
0
20
40
60
80
100
120
-0.5
0
0.5
1
1.5
Time
Manipulated Variable
D

## Slide 25
Class exercise: Comment on the quality of control for the four responses below.
0
20
40
60
80
100
120
-0.5
0
0.5
1
1.5
S-LOOP plots deviation variables (IAE = 17.5417)
Time
Controlled Variable
0
20
40
60
80
100
120
-0.5
0
0.5
1
1.5
2
Time
Manipulated Variable
A
0
20
40
60
80
100
120
-1
0
1
2
3
S-LOOP plots deviation variables (IAE = 43.9891)
Time
Controlled Variable
0
20
40
60
80
100
120
-1
0
1
2
3
4
Time
Manipulated Variable
B
0
20
40
60
80
100
120
-0.5
0
0.5
1
1.5
S-LOOP plots deviation variables (IAE = 34.2753)
Time
Controlled Variable
0
20
40
60
80
100
120
-0.5
0
0.5
1
Time
Manipulated Variable
C
0
20
40
60
80
100
120
-0.5
0
0.5
1
1.5
S-LOOP plots deviation variables (IAE = 24.0376)
Time
Controlled Variable
0
20
40
60
80
100
120
-0.5
0
0.5
1
1.5
Time
Manipulated Variable
D
Too oscillatory
Generally acceptable
Too slow
Gets close quickly;
Gets to set point slowly

## Slide 26
CHAPTER 7: THE FEEDBACK LOOP
We can apply feedback via many approaches
1, No control - The variable responds to all inputs, it “drifts”.
2. Manual - A person observes measurements and introduces changes to compensate, adjustment depends upon the person.
3. On-Off - The manipulated variable has only two states, this results in oscillations in the system.
4. Continuous, automated - This is a modulating control that has corrections related to the error from desired.
5. Emergency - This approach takes extreme action (shutdown) when a dangerous situation occurs.

## Slide 27
CHAPTER 7: THE FEEDBACK LOOP, WORKSHOP 1
The control valve is used to introduce a variable resistance to flow.
What is the body of the valve?
Describe three bodies and what factors are important in selecting.
What is the actuator?
What power source is used? What happens when the power source fails?

## Slide 28
CHAPTER 7: THE FEEDBACK LOOP, WORKSHOP 1
Valve body that includes the stem and the elements in contact with the fluid
Valve actuator that includes the spring and flexible diaphragm
Power source is compressed air
Kuphalt, T. (2012) Lessons in Industrial Instrumentation, http://www.openbookproject.net/books/socratic/sinst/

## Slide 29
CHAPTER 7: THE FEEDBACK LOOP, WORKSHOP 2
Recommend the correct failure position (open or closed) for each of the circled control valves.
air
fuel
feed
product

## Slide 30
CHAPTER 7: THE FEEDBACK LOOP, WORKSHOP 3
Find at least one variable that could be handled by each of the five approaches; no control, manual, on/off, continuous, and emergency.
air
fuel
feed
product

## Slide 31
CHAPTER 7: THE FEEDBACK LOOP, WORKSHOP 4
CA0
CA
A  B
Solvent
Pure A
vc
T
vA
vS
F
V
FC
TCin
TCout
Select several pairs of controlled and manipulated variables for the following process.

## Slide 32
Lot’s of improvement, but we need some more study!
Read the textbook
Review the notes, especially learning goals and workshop
Try out the self-study suggestions
Naturally, we’ll have an assignment!
CHAPTER 7: THE FEEDBACK LOOP
When I complete this chapter, I want to be
able to do the following.
Identify the major elements in the feedback loop
Select appropriate candidate variables to be controlled and manipulated
Evaluate the control performance data using standard measures of dynamic performance

## Slide 33
CHAPTER 7: LEARNING RESOURCES
SITE PC-EDUCATION WEB
- Instrumentation Notes
- Interactive Learning Module (Chapter 7)
- Tutorials (Chapter 7)

## Slide 34
CHAPTER 7: SUGGESTIONS FOR SELF-STUDY
1. Find a sample process in each of your previous courses and select a pair of controlled and manipulated variables
- Heat Transfer (heat exchanger)
- Fluid Mechanics (flow in a pipe
- Mass Transfer (stripper, distillation)
- Reaction Engr. (packed bed reactor)
2. Compare the measures of control performance in this chapter with the seven control objectives given in Chapter 2.
3. Describe the actions you would take if you measured a disturbance and did not want to wait for feedback corrections.