## Slide 1
Process Control: Designing Process and Control Systems for Dynamic Performance
Chapter 10. Stability and Tuning
Copyright © Thomas Marlin 2013
The copyright holder provides a royalty-free license for use of this material at non-profit educational institutions

## Slide 2
CHAPTER 10: STABILITY &TUNING
When I complete this chapter, I want to be
able to do the following.
Determine the stability of a process without control
Determine the stability of a closed-loop feedback control system
Use these approaches to learn how dead time affects stability.

## Slide 3
Outline of the lesson.
Define stability
Review determining the roots of the characteristic equation
Introduce the Bode stability method
Apply to determine some general trends in feedback systems
CHAPTER 10: STABILITY &TUNING

## Slide 4
TC
v1
v2
We influence stability when we implement control. How do we achieve the influence we want?
CHAPTER 10: STABILITY &TUNING
0
20
40
60
80
100
120
-40
-20
0
20
0
20
40
60
80
100
120
-0.2
0
0.2
0.4
0.6
0.8
or
No!
Yes!

## Slide 5
CHAPTER 10: STABILITY &TUNING
First, let’s define stability: A system is stable if all bounded inputs to the system result in bounded outputs.
Process
Sample
Inputs
Sample
Outputs
0
0.5
1
1.5
-1
-0.5
0
0.5
1
0
0.5
1
1.5
-1
-0.5
0
0.5
1
bounded
unbounded
bounded
unbounded

## Slide 6
Let’s review how we
determine the
stability of a model.
G(s) = Y(s)/X(s)
Y(s) = [N(s)/D(s)] X(s)
With i the solution to the denominator of the transfer function being zero, D(s) = 0 giving s = 1, 2 , i ... .
Real, distinct i
Real, repeated i
Complex i
If all i are ???, Y(t) is stable
If any one i is ???, Y(t) is unstable
CHAPTER 10: STABILITY &TUNING
Class exercise

## Slide 7
With i the solutions to D(s) = 0, which is a polynomial.
1. If all real [i] are < 0, Y(t) is stable
If any one real [i] is  0, Y(t) is unstable
2. If all i are real, Y(t) is overdamped (does not oscillate)
If one pair of i are complex, Y(t) is underdamped
CHAPTER 10: STABILITY &TUNING

## Slide 8
CHAPTER 10: STABILITY &TUNING
Gd(s)
GP(s)
Gv(s)
GC(s)
GS(s)
D(s)
CV(s)
CVm(s)
SP(s)
E(s)
MV(s)
+
+
+
-
Transfer functions
GC(s) = controller
Gv(s) = valve +
GP(s) = feedback process
GS(s) = sensor +
Gd(s) = disturbance process
Variables
CV(s) = controlled variable
CVm(s) = measured value of CV(s)
D(s) = disturbance
E(s) = error
MV(s) = manipulated variable
SP(s) = set point
Quick review of model for closed-loop feedback system.

## Slide 9
Gd(s)
GP(s)
Gv(s)
GC(s)
GS(s)
D(s)
CV(s)
CVm(s)
SP(s)
E(s)
MV(s)
+
+
+
-
Set point response
Disturbance Response
CHAPTER 10: STABILITY &TUNING
The denominator determines the stability of
the closed-loop feedback system! We call it the
characteristic equation.

## Slide 10
solvent
pure A
AC
FS
FA
CHAPTER 10: STABILITY &TUNING
Controller is a P-only controller. Is the system stable? Let’s evaluate the roots of the characteristic equation.
Direction Solution for the Roots to determine the stability

## Slide 11
-0.7
-0.6
-0.5
-0.4
-0.3
-0.2
-0.1
0
0.1
-0.5
-0.4
-0.3
-0.2
-0.1
0
0.1
0.2
0.3
0.4
0.5
Real
Imaginary
Stable
Unstable
Kc
250 0
CHAPTER 10: STABILITY &TUNING
As the controller gain, KC, is increased,
some roots approach, then cross the
boundary (s=0) between stable and
Unstable. Shaded is the unstable region.
Plot of real and imaginary parts of the roots of the characteristic equation - three roots for cubic

## Slide 12
CHAPTER 10: STABILITY &TUNING
Set point response
The denominator
determines
the stability of
the closed-loop
feedback system!
Bode Stability Method
Calculating the roots is easy with standard software. However, if the equation has a dead time, the term e -s appears. Therefore, we need another method.
Th method we will use next is the Bode Stability Method.

## Slide 13
CHAPTER 10: STABILITY &TUNING
Bode Stability: To understand, let’s do a thought experiment
solvent
pure A
AC
FS
FA
Loop open
GP(s)
Gv(s)
GC(s)
GS(s)
CV(s)
CVm(s)
SP(s)
E(s)
MV(s)
+
+
+
-
Loop open
SP

## Slide 14
CHAPTER 10: STABILITY &TUNING
Bode Stability: To understand, let’s do a thought experiment
solvent
pure A
AC
FS
FA
Loop closed
GP(s)
Gv(s)
GC(s)
GS(s)
CV(s)
CVm(s)
SP(s)
E(s)
MV(s)
+
+
+
-
Loop closed
No forcing!!
GP(s)
Gv(s)
GC(s)
GS(s)
CV(s)
CVm(s)
SP(s)
E(s)
MV(s)
+
+
+
-
Loop closed
No forcing!!
No forcing!!
SP

## Slide 15
CHAPTER 10: STABILITY &TUNING
Bode Stability: To understand, let’s do a thought experiment
GP(s)
Gv(s)
GC(s)
GS(s)
CV(s)
CVm(s)
SP(s)
E(s)
MV(s)
+
+
+
-
Loop closed
Under what conditions is the system stable (unstable)?
Hint: think about the sine wave as it travels around the loop once.

## Slide 16
CHAPTER 10: STABILITY &TUNING
Bode Stability: To understand, let’s do a thought experiment
GP(s)
Gv(s)
GC(s)
GS(s)
CV(s)
CVm(s)
SP(s)
E(s)
MV(s)
+
+
+
-
Loop closed
Under what conditions is the system stable (unstable)?
If the sine is larger in amplitude after one cycle; then it will increase each “time around” the loop. The system will be unstable.
Now: at what frequency does the sine most reinforce itself?

## Slide 17
CHAPTER 10: STABILITY &TUNING
Bode Stability: To understand, let’s do a thought experiment
GP(s)
Gv(s)
GC(s)
GS(s)
CV(s)
CVm(s)
SP(s)
E(s)
MV(s)
+
+
+
-
Loop closed
Now: at what frequency does the sine most reinforce itself?
When the sine has a lag of 180° due to element dynamics, the feedback will reinforce the oscillation (remember the - sign).
This is the critical frequency.

## Slide 18
CHAPTER 10: STABILITY &TUNING
Bode Stability: To understand, let’s do a thought experiment
GP(s)
Gv(s)
GC(s)
GS(s)
CV(s)
CVm(s)
SP(s)
E(s)
MV(s)
+
+
+
-
Loop closed
Let’s put the results together. GOL(s) includes all elements in the closed loop.
At the critical frequency:  GOL(cj) = -180
The amplitude ratio: |GOL(cj) | < 1 for stability
|GOL(cj) | > 1 for stability
See textbook for limitations

## Slide 19
CHAPTER 10: STABILITY &TUNING
Bode Stability: Let’s do an example: three-tank mixer
with 5 minutes dead time added
 GOL(cj) = -180 |GOL(cj) | < 1 for stability
Process
Controller tuning w/o dead time
From Ciancone correlations

## Slide 20
CHAPTER 10: STABILITY &TUNING
Bode Stability:  GOL(cj) = -180 |GOL(cj) | < 1 for stability
10
-2
10
-1
10
0
10
-1
10
0
10
1
10
2
Frequency, w (rad/time)
Amplitude Ratio
10
-2
10
-1
10
0
-300
-250
-200
-150
-100
-50
Frequency, w (rad/time)
Phase Angle (degrees)
-180
Critical frequency
|GOL(cj) | = 0.75
Conclusion?

## Slide 21
CHAPTER 10: STABILITY &TUNING
Bode Stability:  GOL(cj) = -180 |GOL(cj) | < 1 for stability
10
-2
10
-1
10
0
10
-1
10
0
10
1
10
2
Frequency, w (rad/time)
Amplitude Ratio
10
-2
10
-1
10
0
-300
-250
-200
-150
-100
-50
Frequency, w (rad/time)
Phase Angle (degrees)
-180
Critical frequency
|GOL(cj) | = 0.75 < 1
Conclusion:
stable!!
The sine will decrease in amplitude each time around the loop.

## Slide 22
CHAPTER 10: STABILITY &TUNING
0
50
100
150
200
250
0
0.5
1
1.5
2
S-LOOP plots deviation variables (IAE = 42.1962)
Time
Controlled Variable
0
50
100
150
200
250
0
20
40
60
Time
Manipulated Variable
Stable, but
performance
poor, why?

## Slide 23
CHAPTER 10: STABILITY &TUNING
0
50
100
150
200
250
0
0.5
1
1.5
2
S-LOOP plots deviation variables (IAE = 42.1962)
Time
Controlled Variable
0
50
100
150
200
250
0
20
40
60
Time
Manipulated Variable
Stable, but
performance
poor, why?
PI tuning was for the process without dead time. The process with dead time is more difficult to control. Must make controller less agressive!
Key lesson: Stability is required, but more is required for good performance.

## Slide 24
*************************************************
Critical frequency and amplitude ratio
from Bode plot of GOL
*************************************************
Caution: 1) cross check with plot because of possible
MATLAB error in calculating the phase angle
2) the program finds the first crossing of -180
The critical frequency is between 0.14263
and 0.14287
The amplitude ratio at the critical frequency is 0.74797
10
-2
10
-1
10
0
10
-1
10
0
10
1
10
2
Frequency, w (rad/time)
Amplitude Ratio
10
-2
10
-1
10
0
-300
-250
-200
-150
-100
-50
Frequency, w (rad/time)
Phase Angle (degrees)
*************************************************************
* S_LOOP: SINGLE LOOP CONTROL SYSTEM ANALYSIS *
* BODE PLOT OF GOL(s) = Gp(s)Gc(s) *
* *
* Characteristic Equation = 1 + GOL(s) *
*************************************************************
SELECT THE APPROPRIATE MENU ITEM
MODIFY...
PRESENT VALUES
1) Lowest Frequency 0.01
2) Highest Frequency 0.30
3) Create Bode plot
and calculate the results at critical frequency
4) Return to main menu
Enter the desired selection:
Bode calculations can be done by hand, easier with S_LOOP
Or, write your own program in MATLAB.

## Slide 25
CHAPTER 10: STABILITY &TUNING
We can evaluate the stability of a process without control by evaluating the roots of char. equation
We can evaluate the stability of a process under feedback by either
- evaluating the roots of char. equation
- Bode method (required for process with dead time)
These are local tests, caution about non-linearity
Stability does not guarantee good performance !!!!
Unstable system performance always poor!!!
Let’s review what we have accomplished so far.

## Slide 26
CHAPTER 10: STABILITY &TUNING
What else can we do with this neat technology?
Tune controllers
Ziegler-Nichols Tuning
We can tune controllers. The basic idea is to keep a “reasonable” margin from instability limit. This “reasonable” margin might give good performance.
solvent
pure A
AC
FS
FA

## Slide 27
CHAPTER 10: STABILITY &TUNING
What else can we do with this neat technology?
Tune controllers
Controller | Kc | TI | Td
P-only | Ku/2 | --- | ---
PI | Ku/2.2 | Pu/1.2 | ---
PID | Ku/1.7 | Pu/2.0 | Pu/8
Gain margin is approximately 2
Integral mode is required for zero s-s offset
Derivative has stabilizing effect

## Slide 28
CHAPTER 10: STABILITY &TUNING
solvent
pure A
AC
FS
FA
0
50
100
150
200
250
0
0.5
1
1.5
2
S-LOOP plots deviation variables (IAE = 23.3131)
Time
Controlled Variable
0
50
100
150
200
250
-50
0
50
100
150
Time
Manipulated Variable
Ziegler-Nichols tuning
Generally, Ziegler-Nichols tuning is not the best initial tuning method.
However, these two guys were real pioneers in the field! It has taken 50 years to surpass their guidelines.

## Slide 29
CHAPTER 10: STABILITY &TUNING
What else can we do with this neat technology?
Understand why detuning is required for tough processes.
0.1
1
10
KcKp
0
0.2
0.4
0.6
0.8
1
fraction dead time
Ziegler-Nichols
Ciancone
As dead time
increases, we
must detune
the controller.
In this plot, (+) is constant and / (+) is changed.

## Slide 30
CHAPTER 10: STABILITY &TUNING
What else can we do with this neat technology?
Understand need for “robustness”.
After we tune the controller,
we change the flow of solvent.
What happens?
solvent
pure A
AC
FS
FA
FS = 3.0 to 6.9 m3/min

## Slide 31
CHAPTER 10: STABILITY &TUNING
10
-2
10
-1
10
0
10
-5
10
0
frequency (rad/time)
amplitude ratio
10
-2
10
-1
10
0
-300
-200
-100
0
frequency (rad/time)
phase angle
-180
Range of critical frequencies. Smallest is most conservative
Must consider the
model error when
selecting controller
tuning
What else can we do with this neat technology?
Understand need for “robustness”.

## Slide 32
CHAPTER 10: STABILITY &TUNING
solvent
pure A
AC
FS
FA
FS = 3.0 to 6.9 m3/min
Tune for the process response that is slowest,
has highest fraction dead time, and largest
process gain.
This will give least aggressive controller.
What else can we do with this neat technology?
Understand need for “robustness”.

## Slide 33
CHAPTER 10: STABILITY &TUNING
Match your select of tuning method to tuning goals!

## Slide 34
0
5
10
15
20
25
30
35
40
45
50
-1
0
1
2
3
4
Time
Controlled Variable
0
5
10
15
20
25
30
35
40
45
50
0
5
10
15
Time
Manipulated Variable
The data below is a process reaction curve for a process, plotted in deviation variables. Determine the tuning for a PID controller using the Ziegler-Nichols method.
TC
v1
v2
CHAPTER 10: TUNING & STABILITY WORKSHOP 1

## Slide 35
CHAPTER 10: TUNING & STABILITY WORKSHOP 2
Answer true or false to each of the following questions and explain each answer.
A. A closed-loop system is stable only if the process and the controller are both stable.
B. The Bode stability method proves that the closed-loop system is stable for only sine inputs.
C. GOL(s) is the process model, GP(s), and sensor, final element, and signal transmission dynamics
D. A process would be stable if it had three poles with the following values: -1, -.2, and 0.

## Slide 36
CHAPTER 10: TUNING & STABILITY WORKSHOP 3
solvent
pure A
AC
FS
FA
The PID controller has been tuned for a three-tank mixer. Later, we decide to include another mixing tank in the process. If we do not retune the controller, will the control system be stable with the four-tank mixer?
Kc = 30
TI = 11
Td = 0.8

## Slide 37
Lot’s of improvement, but we need some more study!
Read the textbook
Review the notes, especially learning goals and workshop
Try out the self-study suggestions
Naturally, we’ll have an assignment!
CHAPTER 10: STABILITY &TUNING
When I complete this chapter, I want to be
able to do the following.
Determine the stability of a process without control
Determine the stability of a closed-loop feedback control system
Use these approaches to learn how dead time affects stability.

## Slide 38
CHAPTER 10: LEARNING RESOURCES
SITE PC-EDUCATION WEB
- Instrumentation Notes
- Interactive Learning Module (Chapter 10)
- Tutorials (Chapter 10)
S_LOOP
- You can perform the stability and frequency response calculations uses menu-driven features. Then, you can simulate in the time domain to confirm your conclusions.

## Slide 39
CHAPTER 10: SUGGESTIONS FOR SELF-STUDY
1. Determine the stability for the example in textbook Table 9.2 (recommended tuning). Use the nominal process parameters. How much would KC have to be increased until the system became unstable?
2. Determine the Ziegler-Nichols tuning for the three-tank mixer process. Simulate the dynamic response using S_LOOP.
3. Discuss applying the Bode stability method to a process without control.

## Slide 40
CHAPTER 10: SUGGESTIONS FOR SELF-STUDY
4. We do not want to operate a closed-loop system “too close” to the stability limit. Discuss measures of the closeness to the limit and how they could be used in calculating tuning constant values.