## Slide 1
Process Control: Designing Process and Control Systems for Dynamic Performance
Chapter 11. Digital Control
Copyright © Thomas Marlin 2013
The copyright holder provides a royalty-free license for use of this material at non-profit educational institutions

## Slide 2
CHAPTER 11: DIGITAL CONTROL
When I complete this chapter, I want to be
able to do the following.
Identify examples of analog and digital computation and signal transmission.
Program a digital PID calculation
Select a proper execution rate for a feedback controller.
Tune a digital PID

## Slide 3
Outline of the lesson.
Brief history of control equipment
Sampling the measurement
Digital PID calculation
Effect of digital execution period on tuning and performance
CHAPTER 11: DIGITAL CONTROL

## Slide 4
CHAPTER 11: DIGITAL CONTROL
A BRIEF HISTORY OF PROCESS CONTROL
A little history helps us to understand the common approaches to process control. The realities of available equipment have shaped the theory and practice of process control.
While digital technology has revolutionized what is possible today, equipment has a life of many decades. Therefore, we see older approaches in most plants, and will for a long time.
Let’s start from about the late 18th and early 19th century to today. What happened that “got things going”?

## Slide 5
CHAPTER 11: DIGITAL CONTROL
Making the steam engine work all the time
Inventors wanted to control the pressure of the boiler and the speed of the device driven by the steam (using a governor).
People experienced
- Explosions!
- Unstable behavior
And control engineering was born!
http://oldenginehouse.users.btopenworld.com/watt.htm
governor

## Slide 6
CHAPTER 11: DIGITAL CONTROL
Manual operation
Mechanical devices
Pneumatic devices
Electronic devices
Digital calculations
Digital calc. & communication
Manual Operation
People know more than machines, so leave decisions to them.
Emergency cooling
Temperature indicator
Should I adjust the
valve or should
I run?

## Slide 7
CHAPTER 11: DIGITAL CONTROL
Manual operation
Mechanical devices
Pneumatic devices
Electronic devices
Digital calculations
Digital calc. & communication
Mechanical Device
The value of the variable is represented by position of equipment.
Float measures the liquid level
Raising and lowering the gate affects the flowin
Location of the fulcrum determines the gate/level
How do I change the set point?

## Slide 8
CHAPTER 11: DIGITAL CONTROL
Manual operation
Mechanical devices
Pneumatic devices
Electronic devices
Digital calculations
Digital calc. & communication
Pneumatic Device
The value of the variable is proportional to air pressure (50 - 150 C = 3 -15 psi).
TC
v1
v2
The signal is 3-15 psi air pressure in a pipe.
How do I
perform the
PID
calculation?
Air pressure moves flexible diaphragm

## Slide 9
CHAPTER 11: DIGITAL CONTROL
Manual operation
Mechanical devices
Pneumatic devices
Electronic devices
Digital calculations
Digital calc. & communication
Pneumatic & Electronic Devices
Principle of analog computation!
Build a physical system that (approximately) obeys the same model.
Pneumatic - force balance (Newton’s laws)
Electronic - current balance (Kirkoff’s laws)
I wonder what these devices look like.

## Slide 10
CHAPTER 11: DIGITAL CONTROL
Analog computation!
From Harriott, P., Process Control, McGraw-Hill, New York, 1964
Pneumatic
Electronic

## Slide 11
CHAPTER 11: DIGITAL CONTROL
Manual operation
Mechanical devices
Pneumatic devices
Electronic devices
Digital calculations
Digital calc. & communication
Electronic Device
The variable is proportional to current or voltage (50 - 150 C = 4 - 20 mA).
TC
v1
v2
The signal is 4-20 mA transmitted by wire.
I’ll use
analog
computation
again.
Current converted to air pressure to affect valve

## Slide 12
CHAPTER 11: DIGITAL CONTROL
Manual operation
Mechanical devices
Pneumatic devices
Electronic devices
Digital calculations
Digital calc. & communication
Digital Calculation
Digital calculations with electronic transmission.
The signal is 4-20 mA transmitted by wire.
We’ll soon see
how to
calculate PID
digitally.
Current converted to air pressure to affect valve
TC
v1
v2
Digital
PID

## Slide 13
CHAPTER 11: DIGITAL CONTROL
Manual operation
Mechanical devices
Pneumatic devices
Electronic devices
Digital calculations
Digital calc. & communication
Digital Calculation & Communication
Digital calculations with transmission by local area network. Sensor and valve can have microprocessors too!
We soon see
how to
calculate PID
digitally.
v1
v2
Digital
PID
TC
The signal transmitted digitally.
converted to air pressure to affect valve

## Slide 14
CHAPTER 11: DIGITAL CONTROL
Digital control employs a distributed computing network
Why?

## Slide 15
Digital control employs a distributed computing network
CHAPTER 11: DIGITAL CONTROL

## Slide 16
Sensors, local indicators, and valves in the process.
Some actions and automation done here.
Displays of variables, calculations, and commands to valves are in the centralized control center.
Central control room
Let’s remember that control is performed many places; locally and remotely by people and equipment.
CHAPTER 11: DIGITAL CONTROL

## Slide 17
A rough indication of the use of various devices for control calculations for new industrial process control systems.
CHAPTER 11: DIGITAL CONTROL

## Slide 18
Manual operation
Mechanical devices
Pneumatic devices
Electronic devices
Digital calculations
Digital calc. & communication
TC
v1
v2
Digital
PID
CHAPTER 11: DIGITAL CONTROL
The techniques presented will be applicable for digital sampling and calculation. Transmission can be electronic or digital.
Periodically, the measurement is sampled and a calculation is performed.

## Slide 19
CHAPTER 11: DIGITAL CONTROL
Not much
information lost
What happened
here?

## Slide 20
CHAPTER 11: DIGITAL CONTROL
What happened
here?
ALIASING
Aliasing: Sampling much slower than the measurement changes causes significant loss of information.
Engineer should design for sampling “fast enough”.

## Slide 21
CHAPTER 11: DIGITAL CONTROL
We “hold” the last sampled value between control executions.
-1.5
-0.9
-0.3
0.3
0.9
1.5
0
5
10
15
20
25
30
Time
Continuous signal
Signal after the zero-order hold, samples every 2.5 time units
Does the sample/
hold change the
dynamics?

## Slide 22
CHAPTER 11: DIGITAL CONTROL
The red line is the continuous approximation of the signal after the sample & hold. This shows that the effect is to introduce a “dead time” of about t/2.
Continuous signal
Continuous signal that is approximately the output of the hold.
  t/2 due to sampling

## Slide 23
CHAPTER 11: DIGITAL CONTROL
Proportional:
Integral:
Derivative:
Hint: How would you estimate
each mode using numerical
methods?
We have a sample of values; CV1, CV2, …., CVN

## Slide 24
CHAPTER 11: DIGITAL CONTROL
Proportional:
Integral:
Derivative:
We have a sample of values; CV1, CV2, …., CVN
Calculated every time the
controller is executed.

## Slide 25
CHAPTER 11: DIGITAL CONTROL
Proportional:
Integral:
Derivative:
We have a sample of values; CV1, CV2, …., CVN
Calculated every time the
controller is executed.
t = constant
How many elements in sum?

## Slide 26
CHAPTER 11: DIGITAL CONTROL
Proportional:
Integral:
Derivative:
We have a sample of values; CV1, CV2, …., CVN
Efficient calculation in realtime!

## Slide 27
CHAPTER 11: DIGITAL CONTROL
Proportional:
Integral:
Derivative:
We have a sample of values; CV1, CV2, …., CVN
Calculated every time the
controller is executed.

## Slide 28
CHAPTER 11: DIGITAL CONTROL
We have a sample of values; CV1, CV2, …., CVN
Calculated only when
the controller is turned on, N=1.
Thereafter, I is constant
Bumpless transfer:No change to the MV when controller is first executed
“I” is sometimes called the bias.

## Slide 29
CHAPTER 11: DIGITAL CONTROL
Put all modes together.
Digital PID, positional form calculates the output to the final element

## Slide 30
CHAPTER 11: DIGITAL CONTROL
Digital PID, Velocity form - Alternatively, we can calculate the change in the signal at every execution.

## Slide 31
CHAPTER 11: DIGITAL CONTROL
What is the effect of digital execution of the PID controller on tuning and performance?
Hint: things
don’t get
better by
slowing the
loop.
solvent
pure A
AC
FS
FA
SP
Continuous tuning
Kc = 30
TI = 11
Td = 0.80

## Slide 32
CHAPTER 11: DIGITAL CONTROL
0
50
100
150
200
250
0
0.5
1
1.5
S-LOOP plots deviation variables (IAE = 12.2909)
Time
Controlled Variable
0
50
100
150
200
250
0
10
20
30
40
Time
Manipulated Variable
0
50
100
150
200
250
0
0.5
1
1.5
S-LOOP plots deviation variables (IAE = 20.0491)
Time
Controlled Variable
0
50
100
150
200
250
0
20
40
60
Time
Manipulated Variable
0
50
100
150
200
250
0
0.5
1
1.5
2
S-LOOP plots deviation variables (IAE = 37.1005)
Time
Controlled Variable
0
50
100
150
200
250
0
20
40
60
Time
Manipulated Variable
0
50
100
150
200
250
0
0.5
1
1.5
2
S-LOOP plots deviation variables (IAE = 45.5197)
Time
Controlled Variable
0
50
100
150
200
250
-20
0
20
40
60
80
Time
Manipulated Variable
Continuous PID
Digital PID, t=5
Digital PID, t=10
Digital PID, t=15
CONCLUSION: We should retune the controller when the execution is slow compared with the feedback dynamics!

## Slide 33
CHAPTER 11: DIGITAL CONTROL
0
50
100
150
200
250
0
0.5
1
1.5
S-LOOP plots deviation variables (IAE = 12.2909)
Time
Controlled Variable
0
50
100
150
200
250
0
10
20
30
40
Time
Manipulated Variable
0
50
100
150
200
250
0
0.5
1
1.5
S-LOOP plots deviation variables (IAE = 20.0491)
Time
Controlled Variable
0
50
100
150
200
250
0
20
40
60
Time
Manipulated Variable
Continuous PID
Digital PID, t=5
t = 0.33(+) >> 0.05 (+)
Guideline for selecting the execution time:
To prevent degradation of control loop performance, select a controller execution time of t  0.05(+).
Note: Typical sample period for chemical process control is 1/3-1/2 second. Much faster is possible, if needed.

## Slide 34
CHAPTER 11: DIGITAL CONTROL
Modified PID tuning for digital controllers - this is a guideline that usually works adequately.
Continuous signal
Continuous signal that is approximately the output of the hold.
  t/2 due to sampling
We learned that sampling introduces an additional dead time of about t/2.
1. Obtain model, usually using empirical method
2. Determine the sample period, t  0.05(+), if possible
3. Recalculate the dead time as ’ =  + t/2
4. Calculate tuning using continuous method
5. Implement and fine tune as needed

## Slide 35
solvent
pure A
AC
FS
FA
Tuning from chart
Kc = ??
TI = ??
Td = ??
Process reaction curve
Kp = 0.039 %A/%open
 = 5.5 + ?? = ?? min
 = 10.5 min
CHAPTER 11: DIGITAL CONTROL
Let’s apply this guideline for the three-tank mixer with a long sample time = 15 minutes.

## Slide 36
CHAPTER 11: DIGITAL CONTROL
0
50
100
150
200
250
0
0.5
1
1.5
S-LOOP plots deviation variables (IAE = 20.0383)
Time
Controlled Variable
0
50
100
150
200
250
0
10
20
30
40
50
Time
Manipulated Variable
Tuning from chart
Kc = 20
TI = 14
Td = 2.35
IAE increased from 12.2 to 20+
The performance is about as good as possible with this very long sampling time! Would you fine tune further?

## Slide 37
CHAPTER 11: DIGITAL CONTROL
If the PID is no better in digital form, why did we spend decades of engineering time and billions of dollars converting the world’s control to digital?

## Slide 38
CHAPTER 11: DIGITAL CONTROL
Why did we convert the world’s control to digital - Complex controllers
Improved performance can be achieved with algorithms that optimize the path to the set point, every controller execution!
(See Chapters 19 and 23)
FR
FV
0
50
100
150
200
0.98
0.985
0.99
0.995
Distillate Light key
Time
0
50
100
150
200
0.02
0.025
0.03
0.035
0.04
Bottoms Light Key
Time
Good performance!
Almost no disturbance!

## Slide 39
CHAPTER 11: DIGITAL CONTROL
Why did we convert the world’s control to digital - Process monitoring
We have a digital history of measurements for
Recall at any time for trouble shooting
Calculation of process performance indicators, heat transfer coefficients, reactor yields, energy/kg of product, and so forth
Excellent graphical displays with data in context of process schematic
(See Chapter 26)

## Slide 40
CHAPTER 11: DIGITAL CONTROL
Why did we convert the world’s control to digital - Process optimization
(See Chapter 26)
Best product/ recycle purities?
Best suction pressure?
Best reactor conversions?
Best feed rates, each feed type

## Slide 41
CHAPTER 11: DIGITAL CONTROL
Why did we convert the world’s control to digital -Diagnostics
We have digital monitors at sensor, controller and valve!
Compare signal to valve with actual valve position - report significant errors
Diagnose problems with sensor (voltage, etc.)
Do not take feedback control action on questionable loop - alarm operator
And many other
reasons that
digital is
a winner.

## Slide 42
CHAPTER 11: DIGITAL CONTROL, WORKSHOP 1
1. Select all of the appropriate answers. Mechanical implementation of feedback control employs
a. Digital computation
b. Analog computation
c. Neither a nor b
d. Both a and b
2. A digital PID controller is operating “in automatic”, i.e., it is calculating the signal to the final element. You are fine tuning the loop. You change the controller gain by -30% of its original value.
Describe what happens.

## Slide 43
CHAPTER 11: DIGITAL CONTROL, WORKSHOP 2
TC
v1
v2
You are tuning the temperature controller shown in the figure. You have determined the dynamic model below.
Determine the PID tuning for this loop for execution periods below and simulate the results using S_LOOP.
t = 0.10
t = 1.0
t = 5.0
(All times are in minutes.)

## Slide 44
CHAPTER 11: DIGITAL CONTROL, WORKSHOP 3
Develop a table with advantages and disadvantages for the six control equipment categories for many important issues.

## Slide 45
When I complete this chapter, I want to be
able to do the following.
CHAPTER 11: DIGITAL CONTROL
Lot’s of improvement, but we need some more study!
Read the textbook
Review the notes, especially learning goals and workshop
Try out the self-study suggestions
Naturally, we’ll have an assignment!
Identify examples of analog and digital computation and signal transmission.
Program a digital PID calculation
Select a proper execution rate for a feedback controller.
Tune a digital PID

## Slide 46
CHAPTER 11: LEARNING RESOURCES
SITE PC-EDUCATION WEB
- Instrumentation Notes
- Interactive Learning Module (Chapter 11)
- Tutorials (Chapter 11)
Software Laboratory, S_LOOP
- You can simulate a PID loop with continuous of digital control to determine the effect of execution period.

## Slide 47
CHAPTER 11: SUGGESTIONS FOR SELF-STUDY
1. Find some process reaction curve plots in Chapters 3-5. Determine the maximum PID execution period. Then, for a controller execution period ten times the minimum, determine the tuning for PID and PI controllers using the tuning charts.
2. Using S_LOOP, simulate the system(s) in question 1.
3. Develop a flowchart for an excellent computer program to calculate the PID control. This should be a subroutine that can be called for every controller in the plant.

## Slide 48
CHAPTER 11: SUGGESTIONS FOR SELF-STUDY
4. Take an inventory of your house and identify analog and digital control systems.
5. Develop a simulation that accepts a continuous signal and determines the output of a zero-order hold and first-order hold.