## Slide 1
Process Control: Designing Process and Control Systems for Dynamic Performance
Chapter 14. Cascade Control
Copyright © Thomas Marlin 2013
The copyright holder provides a royalty-free license for use of this material at non-profit educational institutions

## Slide 2
CHAPTER 14: CASCADE CONTROL
When I complete this chapter, I want to be
able to do the following.
Identify situations for which cascade is a good control enhancement
Design cascade control using the five design rules
Apply the tuning procedure to cascade control

## Slide 3
Outline of the lesson.
A process challenge - improve performance
Cascade design rules
Good features and application guidelines
Several process examples
Analogy to management principle
CHAPTER 14: CASCADE CONTROL

## Slide 4
TC
2
T
1
F
1
F
2
T
3
L
1
feed
product
heating stream
CHAPTER 14: CASCADE CONTROL
Discuss this
stirred tank
heat exchanger.
PID controller

## Slide 5
CHAPTER 14: CASCADE CONTROL
TC
2
T
1
F
1
F
2
T
3
L
1
feed
heating stream
Disturbance =
heating pressure
Control
performance
not acceptable!
Pressure disturbance
0
20
40
60
80
100
120
140
160
180
200
72
73
74
75
76
IAE = 147.9971 ISE = 285.4111
temperature
minimum
Class exercise: What do
we do?
TC

## Slide 6
CHAPTER 14: CASCADE CONTROL
Let’s think about the process behavior.
Causal relationship from P disturbance to T (without control)
What measurable effect always occurs when P changes?
v (valve)  ???  Q  TC
P
(heating oil)
P

## Slide 7
CHAPTER 14: CASCADE CONTROL
Let’s think about the process behavior.
If we can maintain this variable approximately constant, can we reduce the effect of the disturbance?
v (valve)  ???  Q  TC
P
(heating oil)
P

## Slide 8
TC
2
T
1
F
1
F
2
T
3
L
1
feed
product
heating stream
CHAPTER 14: CASCADE CONTROL
Sketch a
Proposal
here.
PID controller

## Slide 9
TC
2
T
1
F
1
FC
2
T
3
L
1
feed
product
heating stream
CHAPTER 14: CASCADE CONTROL
Key variables
for the two
PID controllers.
SP1 from person
SP2 = MV1
F2=CV2
v=MV2
T2=CV1
A New Control Structure!!
primary
secondary

## Slide 10
CHAPTER 14: CASCADE CONTROL
Define the
calculations
performed in
the computer.
Class exercise
computer
plant
T
2
F
2
computer
person
T2SP

## Slide 11
CHAPTER 14: CASCADE CONTROL
Each controller
is a PID!
Class exercise
computer
plant
T
2
F
2
computer
person
T2SP

## Slide 12
CHAPTER 14: CASCADE CONTROL
Control Performance Comparison for CST Heater
Single-Loop Cascade
0
20
40
60
80
100
120
140
160
180
200
72
73
74
75
76
IAE = 147.9971 ISE = 285.4111
temperature
0
50
100
150
200
72
73
74
75
76
IAE = 11.5025 ISE = 1.6655
Much better
performance!
WHY?

## Slide 13
CHAPTER 14: CASCADE CONTROL
Cascade Control Performance for CST Heater
WHY?
Disturbance in
flow is quickly
corrected.
This compensates for
the disturbance!
0
50
100
150
200
72
73
74
75
76
IAE = 11.5025 ISE = 1.6655
temperature
0
50
100
150
200
18
18.5
19
19.5
20
20.5
IAE = 11.6538 ISE = 11.2388
Time
heating flow
0
50
100
150
200
50
52
54
56
58
SAM = 5.8711 SSM = 4.4807
Time
heating valve (% open)
TC
FC
Valve adjustment is not aggressive!
Disturbance affects flow sooner than T2
Small deviation, returns to set point

## Slide 14
CHAPTER 14: CASCADE CONTROL
TC
2
T
1
F
1
FC
2
T
3
L
1
feed
product
heating stream
SP1 for person
SP2 = MV1
CV2
MV2
CV1
What have we gained and lost using cascade control?
For each case, is cascade better, same, worse than single-loop feedback (TC2  v)?
A disturbance in heating medium inlet pressure
A disturbance in heating medium inlet temperature
A disturbance in feed flow rate
A change to the TC set point

## Slide 15
CHAPTER 14: CASCADE CONTROL
TC
2
T
1
F
1
FC
2
T
3
L
1
feed
product
heating stream
SP1 for person
SP2 = MV1
CV2
MV2
CV1
What have we gained and lost using cascade control?
For each case, is cascade better, same, worse than single-loop feedback (TC2  v)?
A disturbance in heating medium inlet pressure
A disturbance in heating medium inlet temperature
A disturbance in feed flow rate
A change to the TC set point
Cascade better
Both the same
Both the same
Both the same

## Slide 16
CHAPTER 14: CASCADE CONTROL
CASCADE DESIGN CRITERIA
Cascade is desired when
1. Single-loop performance unacceptable
2. A measured variable is available
A secondary variable must
3. Indicate the occurrence of an important disturbance
4. Have a causal relationship from valve to secondary (cause  effect)
5. Have a faster response than the primary
Very important

## Slide 17
CHAPTER 14: CASCADE CONTROL
ADVANTAGES OF CASCADE CONTROL
Large improvement in performance when the secondary is much faster than primary
Simple technology with PID algorithms
Use of feedback at all levels. Primary has zero offset for “step-like” disturbances.
Plant operating personnel find cascades easy to operate. Open a cascade at one level, and all controllers above are inactive.

## Slide 18
CHAPTER 14: CASCADE CONTROL
CLASS EXERCISE: SOME QUESTIONS ABOUT CASCADE CONTROL
Why do we retain the primary controller?
Which modes are required for zero steady-state offset?
Which modes are recommended?
What is the additional cost for cascade control?
Normally, each PID controller represents one independent controlled variable. Is anything different in a cascade structure?
What procedure is used for tuning cascade control?

## Slide 19
CHAPTER 14: CASCADE CONTROL
Discuss this
packed bed
reactor.

## Slide 20
CHAPTER 14: CASCADE CONTROL
Class exercise: Design a cascade control structure to improve performance.
feed
product
heating stream
packed bed
reactor
AC
1
T
3
T
2
F
2
F
1
T
1
A
2
0
100
200
300
400
500
-0.05
0
0.05
0.1
0.15
0.2
CV1
maximum
Performance
not acceptable
AC
Disturbance in heating medium temperature

## Slide 21
CHAPTER 14: CASCADE CONTROL
Class exercise: Design a cascade control structure to improve performance.
Let’s use the
cascade design
rules!
Remember: The disturbance is the heating medium inlet temperature and the primary is AC-1.

## Slide 22
CHAPTER 14: CASCADE CONTROL
Class exercise: Design a cascade control structure to improve performance.
Let’s use the
cascade design
rules!
T3 satisfies all of the rules and can be used as a secondary in a cascade.
T2 is the disturbance but cannot be used in cascade!

## Slide 23
CHAPTER 14: CASCADE CONTROL
Sketch your
design on this
drawing.

## Slide 24
feed
product
heating stream
packed bed
reactor
AC
1
TC
3
T
2
F
2
F
1
T
1
A
2
CHAPTER 14: CASCADE CONTROL
SP1 from
person
SP2 = MV1
CV2
MV2
CV1
primary
secondary

## Slide 25
CHAPTER 14: CASCADE CONTROL
Control Performance Comparison for Packed Bed Reactor
Single-Loop Cascade
0
100
200
300
400
500
-0.05
0
0.05
0.1
0.15
0.2
IAE = 24.4229 ISE = 3.4639
CV1
0
100
200
300
400
500
-0.05
0
0.05
0.1
0.15
0.2
IAE = 6.3309 ISE = 0.19017
Much better
performance!
WHY?

## Slide 26
CHAPTER 14: CASCADE CONTROL
Cascade Control Performance for Packed Bed Reactor
0
100
200
300
400
500
-0.05
0
0.05
0.1
0.15
0.2
IAE = 6.3309 ISE = 0.19017
CV1
0
100
200
300
400
500
-1
-0.5
0
0.5
IAE = 37.2971 ISE = 18.6031
Time
CV2
0
100
200
300
400
500
0
1
2
3
4
SAM = 4.3428 SSM = 0.59949
Time
MV
WHY?
Disturbance in
temperature is quickly
corrected.
This compensates for
the disturbance!
AC
TC
Valve adjustment is not aggressive!
Disturbance affects T sooner

## Slide 27
CHAPTER 14: CASCADE CONTROL
What have we gained and lost using cascade control?
How does the system respond to the following?
A disturbance in T1
A disturbance in heating medium inlet pressure
A disturbance in feed pressure
A disturbance to feed composition, A2
A change to the AC-1 set point

## Slide 28
CHAPTER 14: CASCADE CONTROL
What have we gained and lost using cascade control?
How does the system respond to the following?
A disturbance in T1
A disturbance in heating medium inlet pressure
A disturbance in feed pressure
A disturbance to feed composition, A2
A change to the AC-1 set point
Cascade better
Both the same
A disturbance in T1
A disturbance in heating medium inlet pressure
A disturbance in feed pressure
A disturbance to feed composition, A2
A change to the AC-1 set point
Cascade better
Cascade better, but not “perfect”
Both the same

## Slide 29
feed
product
AC
1
TC
3
T
2
F
2
F
1
T
1
A
2
CHAPTER 14: CASCADE CONTROL
SP1 from
person
SP2 = MV1
CV2
CV1
SP3 = MV2
CV3
No limit to number
of levels of cascade!
Each must
meet criteria.
MV3
Three-Level Cascade!

## Slide 30
CHAPTER 14: CASCADE CONTROL
Does cascade apply to instrumentation? Yes, a valve positioner is a secondary that reduces effects of friction!!
TC
2
T
1
F
1
T
3
L
1
feed
product
heating stream
Valve positioner: Measures the stem position and adjusts the air pressure to (closely) achieve the desired position. This is located at the valve.

## Slide 31
CHAPTER 14: CASCADE CONTROL
Does cascade apply to instrumentation? Yes, a valve positioner is a secondary that reduces effects of friction!!
Kuphalt, T. (2012) Lessons in Industrial Instrumentation, http://www.openbookproject.net/books/socratic/sinst/

## Slide 32
CHAPTER 14: CASCADE CONTROL
A cascade is a hierarchy, with decisions transmitted from upper to lower levels.
What are advantages of a hierarchy?
What information should be transmitted up the hierarchy?
What information should flow from secondary to primary in a cascade?

## Slide 33
CHAPTER 14: CASCADE CONTROL WORKSHOP 1
TC
2
T
1
F
1
F
2
T
3
L
1
feed
product
heating stream
Evaluate cascade control for a disturbance in the heating medium inlet temperature. You may add a sensor but make no other changes to the equipment.

## Slide 34
CHAPTER 14: CASCADE CONTROL WORKSHOP 2
TC
2
T
1
F
1
FC
2
T
3
L
1
feed
product
heating stream
SP1 for person
SP2 = MV1
CV2
MV2
CV1
Prepare a detailed plan for tuning the two cascade controllers shown in the following sketch.

## Slide 35
CHAPTER 14: CASCADE CONTROL WORKSHOP 3
Prepare a flowchart for the calculations performed by the packed bed cascade controllers. Show every calculation and use process variable symbols (e.g., A1), not generic symbols (CV1).

## Slide 36
CHAPTER 14: CASCADE CONTROL WORKSHOP 4
Identify process examples in which a valve positioner will improve performance and not improve performance.
Draw a sketch of each process and discuss your recommendation of whether or not to use a positioner.
Note: Modern positioners provide diagnosis of the valve behavior that can be transmitted digitally for later evaluation. This can be very useful in maintenance and trouble shooting.

## Slide 37
Lot’s of improvement, but we need some more study!
Read the textbook
Review the notes, especially learning goals and workshop
Try out the self-study suggestions
Naturally, we’ll have an assignment!
CHAPTER 14: CASCADE CONTROL
When I complete this chapter, I want to be
able to do the following.
Identify situations for which cascade is a good control enhancement
Design cascade control using the five design rules
Apply the tuning procedure to cascade control

## Slide 38
CHAPTER 14: LEARNING RESOURCES
SITE PC-EDUCATION WEB
- Instrumentation Notes
- Interactive Learning Module (Chapter 14)
- Tutorials (Chapter 14)
S_LOOP
- Dynamic simulation of linear system
The Textbook, naturally, for many more examples

## Slide 39
CHAPTER 14: SUGGESTIONS FOR SELF-STUDY
1. Prove that an integral mode is required for zero steady-state offset of the primary.
Do we achieve zero offset for the secondary. Why or why not?
Is there any advantage for achieving zero offset for the secondary?
2. Program a cascade control for one of the processes modelled in Chapters 3-5.
3. Determine a guideline for how much faster the secondary must be than the primary for cascade to function well.

## Slide 40
CHAPTER 14: SUGGESTIONS FOR SELF-STUDY
4. Using block diagram algebra, derive the transfer functions in textbook equations (14.6) to (14.8).
5. Review the following publication to find other advantages for cascade control.
Verhaegen, S., When to use cascade control, Intech, 38-40 (Oct. 1991).
6. Discuss applications of cascade control (hierarchical decision systems) in business, government, and university. Explain advantages and disadvantages of these systems.