## Slide 1
Process Control: Designing Process and Control Systems for Dynamic Performance
Chapter 15. Feedforward Control
Copyright © Thomas Marlin 2013
The copyright holder provides a royalty-free license for use of this material at non-profit educational institutions

## Slide 2
CHAPTER 15: FEEDFORWARD CONTROL
When I complete this chapter, I want to be
able to do the following.
Identify situations for which feedforward is a good control enhancement
Design feedforward control using the five design rules
Apply the feedforward principle to other challenges in life

## Slide 3
Outline of the lesson.
A process challenge - improve performance
Feedforward design rules
Good features and application guidelines
Several process examples
Analogy to management principle
CHAPTER 15: FEEDFORWARD CONTROL

## Slide 4
TC
2
T
1
F
1
F
2
T
3
L
1
feed
product
heating stream
Discuss this
stirred tank
heat exchanger.
PID controller
CHAPTER 15: FEEDFORWARD CONTROL

## Slide 5
TC
2
T
1
F
1
F
2
T
3
L
1
feed
heating stream
Disturbance =
feed temperature
Control
performance
not acceptable!
Class exercise: What do
we do?
CHAPTER 15: FEEDFORWARD CONTROL
0
20
40
60
80
100
120
140
160
180
200
70
72
74
76
IAE = 237.6971 ISE = 758.425
temperature
minimum
TC
Let’s use
cascade

## Slide 6
CHAPTER 15: FEEDFORWARD CONTROL
CASCADE DESIGN CRITERIA FOR T1
Cascade is desired when
1. Single-loop performance unacceptable
2. A measured variable is available
A secondary variable must
3. Indicate the occurrence of an important disturbance
4. Have a causal relationship from valve to secondary
5. Have a faster response than the primary
OK
OK
OK
NO!
Cascade not possible. We need another enhancement!

## Slide 7
TC
2
T
1
F
1
F
2
T
3
L
1
feed
product
heating stream
Let’s think about the process behavior.
Causal relationship from T1 disturbance to T2 (without control)
How can we manipulate valve to compensate?
v (valve)  Q  TC
T0
(Feed temperature)
CHAPTER 15: FEEDFORWARD CONTROL

## Slide 8
0
20
40
60
80
100
120
140
160
180
200
66
68
70
72
74
76
T
0
20
40
60
80
100
120
140
160
180
200
Time
T0
Time
Dm(t) = T0
CVB(t) = compensation effect
CHAPTER 15: FEEDFORWARD CONTROL
We want to
adjust the
valve to
cancel the
effect of the
disturbance.
CVA(t) = disturbance effect
CVA + CVB = no deviation
0
20
40
60
80
100
120
140
160
180
200
50
52
54
56
58
60
v
MV(t) = v

## Slide 9
CHAPTER 15: FEEDFORWARD CONTROL
We use block diagram algebra to determine the form of the calculation [Gff(s)] to achieve the desired performance.
Gd(s)
Gp(s)
Gff(s)
+
Dm(s)
CV A(s)
CV B(s)
CV (s)
MV (s)
Measured disturbance, T0
Manipulated variable
Controlled
variable, T
How do we
measure CVA?
Feedforward
controller

## Slide 10
CHAPTER 15: FEEDFORWARD CONTROL
Not a PID
algorithm!
Why?
??
This is general!

## Slide 11
CHAPTER 15: FEEDFORWARD CONTROL
Dead time
Gain
Lead-lag
Special case of Gp(s) and Gd(s) being first order with dead time
Please
verify.

## Slide 12
CHAPTER 15: FEEDFORWARD CONTROL
Lead-lag = (Tlds+1)/Tlgs+1)
FF controller gain = Kff = - Kd/Kp
controller dead time = ff = d - p  0
Lead time = Tld = p
Lag time = Tlg = d
How do we get values for these parameters?

## Slide 13
CHAPTER 15: FEEDFORWARD CONTROL
Digital implementation is straightforward.
Its derived in textbook.

## Slide 14
CHAPTER 15: FEEDFORWARD CONTROL
Typical dynamic responses from the lead-lag element in the feedforward controller. It synchronizes the compensation and disturbance effects.
Results for several cases of Tlead/Tlag :
a. 0.0
b. 0.5
c. 1.0
d. 1.5
e. 2.0

## Slide 15
CHAPTER 15: FEEDFORWARD CONTROL
TC
2
T
1
F
1
F
2
T
3
L
1
feed
heating stream
TY
1
TY
2
+
FF
FF high-
lighted
in red
How do we combine
feedback with
feedforward?
MVff
MVfb

## Slide 16
Control Performance Comparison for CST Heater
Single-Loop Feedforward with feedback
Much better
performance!
WHY?
CHAPTER 15: FEEDFORWARD CONTROL
0
20
40
60
80
100
120
140
160
180
200
70
72
74
76
IAE = 237.6971 ISE = 758.425
temperature
0
20
40
60
80
100
120
140
160
180
200
70
71
72
73
74
75
76
IAE = 27.772 ISE = 8.0059
temperature

## Slide 17
0
20
40
60
80
100
120
140
160
180
200
74.4
74.6
74.8
75
75.2
75.4
IAE = 27.772 ISE = 8.0059
temperature
0
20
40
60
80
100
120
140
160
180
200
50
52
54
56
58
60
SAM = 11.4394 SSM = 774.0613
Time
heating valve (% open)
CHAPTER 15: FEEDFORWARD CONTROL
TC
The MV changed before T
deviated from its set point!
Disturbance occurred at this time
Valve adjustment not too aggressive
T1
Why wait after disturbance?

## Slide 18
CHAPTER 15: FEEDFORWARD CONTROL
What have we gained and lost using feedforward and feedback?
For each case, is FF with FB better, same, worse than single-loop feedback (TC2  v)??
A disturbance in feed inlet temperature
A disturbance in heating medium inlet pressure
A disturbance in feed flow rate
A change to the TC set point
TC
2
T
1
F
1
F
2
T
3
L
1
feed
heating stream
TY
1
TY
2
+
FF

## Slide 19
CHAPTER 15: FEEDFORWARD CONTROL
What have we gained and lost using feedforward and feedback?
For each case, is FF and FB better, same, worse than single-loop feedback (TC2  v)??
A disturbance in feed inlet temperature
A disturbance in heating medium inlet pressure
A disturbance in feed flow rate
A change to the TC set point
TC
2
T
1
F
1
F
2
T
3
L
1
feed
heating stream
TY
1
TY
2
+
FF
FF/FB better
Both the same
Both the same
Both the same

## Slide 20
FEEDFORWARD DESIGN CRITERIA
Feedforward is desired when
1. Single-loop performance unacceptable
2. A measured variable is available
A measured disturbance variable must
3. Indicate the occurrence of an important disturbance
4. NOT have a causal relationship from valve to measured disturbance sensor
5. Not have a much faster effect on the CV than the MV (when combined with feedback)
CHAPTER 15: FEEDFORWARD CONTROL

## Slide 21
CHAPTER 15: FEEDFORWARD CONTROL
Feedforward and Feedback are complementary

## Slide 22
CLASS EXERCISE: SOME QUESTIONS ABOUT FEEDFORWARD CONTROL
Why do we retain the feedback controller?
When would feedforward give zero steady-state offset?
Why does the feedforward controller sometimes delay its compensation? Don’t we always want fast control?
What is the additional cost for feedforward control?
How can we design a strategy that has two controllers both adjusting the same valve?
What procedure is used for tuning feedforward control?
CHAPTER 15: FEEDFORWARD CONTROL

## Slide 23
CHAPTER 15: FEEDFORWARD CONTROL
Discuss this
packed bed
reactor.

## Slide 24
CHAPTER 15: FEEDFORWARD CONTROL
feed
product
heating stream
packed bed
reactor
AC
1
T
3
T
2
F
2
F
1
T
1
A
2
Performance
not acceptable for
feed composition
disturbance
Class exercise: Design feedforward control to improve the performance.
0
100
200
300
400
500
-0.05
0
0.05
0.1
0.15
0.2
IAE = 22.9349 ISE = 3.0248
CV1
maximum
AC
What about
cascade?
Disturbance in feed composition

## Slide 25
Let’s use the
feedforward
design
rules!
Remember: The disturbance is the feed composition.
Class exercise: Design feedforward control to improve the performance.
CHAPTER 15: FEEDFORWARD CONTROL

## Slide 26
Class exercise: Design feedforward control to improve the performance.
CHAPTER 15: FEEDFORWARD CONTROL
A2 satisfies all of the rules and can be used as a feedforward variable.

## Slide 27
CHAPTER 15: FEEDFORWARD CONTROL
feed
product
heating stream
packed bed
reactor
AC
1
T
3
T
2
F
2
F
1
T
1
A
2
SP1 from
person
MVfb
CV1
AY
2
AC
1
+
MVff
MV
FF
Dm

## Slide 28
Control Performance Comparison for Packed Bed Reactor
Single-Loop Feedforward and feedback
CHAPTER 15: FEEDFORWARD CONTROL
Much better
performance!
WHY?
0
100
200
300
400
500
-0.03
-0.02
-0.01
0
0.01
IAE = 2.1794 ISE = 0.017852
Little model error, most experimental feedforward not this good!
0
100
200
300
400
500
-0.05
0
0.05
0.1
0.15
0.2
IAE = 22.9349 ISE = 3.0248
CV1
AC
AC

## Slide 29
What have we gained and lost using feedforward and feedback?
How does the system respond to the following?
A disturbance in T2
A disturbance in heating medium inlet pressure
A disturbance inT1
A disturbance to feed composition, A2
A change to the AC-1 set point
CHAPTER 15: FEEDFORWARD CONTROL
feed
product
heating stream
packed bed
reactor
AC
1
T
3
T
2
F
2
F
1
T
1
A
2
SP1 from
person
MVfb
CV1
AY
2
AC
1
+
MVff
MV
FF
Dm
Both the same
FF/FB better
Both the same
Both the same
Both the same

## Slide 30
CHAPTER 15: FEEDFORWARD CONTROL
feed
heating stream
packed bed
reactor
AC
1
TC
3
T
2
F
2
F
1
T
1
A
2
SP1 from
person
MV1
CV2
MV2
CV1
primary
secondary
AY
2
TY
3
MVff
We can combine cascade and feedforward to gain the advantages of both.

## Slide 31
CHAPTER 15: FEEDFORWARD CONTROL
Ratio control is a simple and frequently used feedforward application. In ratio control, the dynamics are negligible.
FC
1
FY
1
F
2
Desired F1/F2 = R
x
Blended flow
Uncontrolled
(wild) flow
Manipulated
flow
Goal is to keep
F1/F2
constant.
SPF1 = F2*R

## Slide 32
CHAPTER 15: FEEDFORWARD CONTROL
CLASS EXERCISE: Use analyzer in automatic control while retaining the good aspects of ratio control.
FC
1
FY
1
F
2
Desired F1/F2 = R
x
Blended flow
Uncontrolled
(wild) flow
Manipulated
flow
Goal is to keep
A1
constant.
SPF1 = F2*R
A
1

## Slide 33
CHAPTER 15: FEEDFORWARD CONTROL
CLASS EXERCISE: Use analyzer in automatic control while retaining the good aspects of ratio control.
FC
1
FY
1
F
2
R
x
Blended flow
Uncontrolled
(wild) flow
Manipulated
flow
Goal is to keep
A1
constant.
SPF1 = F2*R
AC
1
Feedback PID

## Slide 34
CHAPTER 15: FEEDFORWARD CONTROL
In many organizations, we take actions on inputs to prevent large disturbances to outputs. Sometimes, these are called “pre-actions”.
After you have measured the change, you have some time to react before it hits you
What would you do if?
Number of births per year increases by 10% in your country
A drought occurs in in the most fertile area of your country
New legislation will impose stricter emissions regulations in three years
Do we need feedback? What is your algorithm? What would you do if the measurement were noisy?

## Slide 35
CHAPTER 15: FEEDFORWARD WORKSHOP 1
TC
2
T
1
F
1
F
2
T
3
L
1
feed
product
heating stream
Evaluate feedforward control for a disturbance in the heating medium inlet temperature. You may add a sensor but make no other changes to the equipment.

## Slide 36
CHAPTER 15: FEEDFORWARD WORKSHOP 2
Prepare a flowchart for the calculations performed by the packed bed feedforward controller. Show every calculation and use process variable symbols (e.g., A1), not generic symbols (CV1). Report the equations for digital control.
feed
heating stream
packed bed
reactor
AC
1
T
3
T
2
F
2
F
1
T
1
A
2
SP1 from
person
MVfb
CV1
AY
2
AC
1
+
MVff
MV
FF
Dm

## Slide 37
CHAPTER 15: FEEDFORWARD WORKSHOP 3
Answer each of the following questions true or false
1. The feedback controller tuning does not change when combined with feedforward compensation.
2. The feedforward controller has no tuning parameter.
3. The feedforward controller should react immediately when the measured disturbance is measured.
4. Feedforward could be applied for a set point change.

## Slide 38
CHAPTER 15: FEEDFORWARD WORKSHOP 4
Identify a process that would benefit from ratio control. You may select from examples in your summer/co-op jobs, engineering laboratories, and course projects.
Draw a sketch of the process with ratio control. Explain the advantages and any disadvantages of the design.

## Slide 39
Lot’s of improvement, but we need some more study!
Read the textbook
Review the notes, especially learning goals and workshop
Try out the self-study suggestions
Naturally, we’ll have an assignment!
CHAPTER 15: FEEDFORWARD
When I complete this chapter, I want to be
able to do the following.
Identify situations for which feedforward is a good control enhancement
Design feedforward control using the five design rules
Apply the feedforward principle to other challenges in life

## Slide 40
CHAPTER 15: LEARNING RESOURCES
SITE PC-EDUCATION WEB
- Instrumentation Notes
- Interactive Learning Module (Chapter 15)
- Tutorials (Chapter 15)
The Textbook, naturally, for many more examples

## Slide 41
CHAPTER 15: SUGGESTIONS FOR SELF-STUDY
1. Suggest some methods for fine-tuning a feedforward controller.
2. Program a feedforward controller for one of the processes modelled in Chapters 3-5.
3. Explain why the feedforward compensation should not be much slower than the disturbance. Why doesn’t this guideline apply when no feedback is implemented?
4. Discuss whether you would recommend more than one feedforward controller on the same process.
5. Write a memorandum explaining feedforward compensation for a company with non-technical employees

## Slide 42
CHAPTER 15: SUGGESTIONS FOR SELF-STUDY
6. A friend asks whether the general sketch for feedback, textbook Figure 1.4, applies to feedforward. Answer completely, including any changes to the sketch.
7. Discuss why the feedforward controller dead time must be positive.